## Summary
System Name: |  | MEADOW MOUNTAIN WS | [5 empty] | Treatment: |  | Slow Sand/DE/Other
PWSID: |  | CO0207504 |  | Monitoring Period (Month/ Year): | [5 empty] | 2009-10-01
State Assigned ID (Plant ID): |  |  | 001
Plant Address: |  | 137 Meadow Mountain Drive |  |  |  | City: | Allenspark |  |  |  |  | Zip: | 80510
Contact Name: |  | Rachel Barkworth |  |  |  | Phone#: |  | 303-823-2318
Combined Filter Effluent Turbidity (CFE) Summary: | [8 empty] | Violation? | Plant off entire month:
↓
| Number of Samples Required*: | [5 empty] | 1
| Number of Samples Taken: | [5 empty] | 31 |  | No
| Number of Samples Exceeding 5 NTU: | [5 empty] | 0 |  | No
| Highest Single Turbidity Reading: | [5 empty] | 0.33 |  | No
| Number of Samples Exceeding 1 NTU (95% limit): | [5 empty] | 0 |  | No
| % of Samples Exceeding 1 NTU: | [5 empty] | 0% |  | No
Entry Point Residual Disinfectant (EPRD) Summary: | [5 empty] | State Assigned ID: |  |  | 001 |  |  | Violation? | For Use by State:
For Chlorine or Chloramine
↓
| Number of Samples Required: | [9 empty] | 1
| Number of Samples Taken: | [9 empty] | 31 | No
| Number of Samples under 0.2 mg/L (Federal level): | [9 empty] | 1 | Yes
| If applicable, number of Samples under |  |  |  | mg/L (State Defined level):
= Required for data processing
number required per day
X
number of days in month
number of plant offlines (PO)
minus
*Samples Required=
Free
Total

## Data Sheet
System Name: |  |  | MEADOW MOUNTAIN WS |  |  |  |  | PWSID: | CO0207504 |  | State Assigned ID: |  |  | 001 | Monitoring Period: |  | 2009-10-01
Required Number of Turbidity Readings Per Day: | [6 empty] | 1 |  | Required Number of Chlorine Readings Per Day: | [6 empty] | 1
| Combined Filter Effluent Turbidity (NTU) | [7 empty] | Entry Point Residual Disinfection (mg/L) | [6 empty] | Comments*
Day | 12-4a Time: ___ | 4a-8a Time: ___ | 8a-12 Time: _____ | 12-4p Time: ____ | 4p-8p Time: ____ | 8p-12 Time: ____ | Highest Turbidity Reading | Highest Reading Time | 12-4a Time: ______ | 4a-8a Time: ______ | 8a-12 Time: ______ | 12-4p Time: ______ | 4p-8p Time: ______ | 8p-12 Time: ______ | Lowest Residual Reading
1 |  |  | 0.28 |  |  |  | 0.28 | 8:15 |  |  | 1 |  |  |  | 1
2 |  |  |  | 0.19 |  |  | 0.19 | 15:45 |  |  |  | 0.8 |  |  | 0.8
3 |  |  |  | 0.21 |  |  | 0.21 | 14:30 |  |  |  | 0.9 |  |  | 0.9
4 |  |  | 0.17 |  |  |  | 0.17 | 11:00 |  |  | 0.6 |  |  |  | 0.6
5 |  |  |  |  | 0.14 |  | 0.14 | 17:15 |  |  |  |  | 0.8 |  | 0.8
6 |  |  | 0.18 |  |  |  | 0.18 | 10:30 |  |  | 0.7 |  |  |  | 0.7
7 |  |  |  | 0.2 |  |  | 0.2 | 14:00 |  |  |  | 1 |  |  | 1
8 |  |  | 0.15 |  |  |  | 0.15 | 11:00 |  |  | 1 |  |  |  | 1
9 |  |  | 0.2 |  |  |  | 0.2 | 11:30 |  |  | 0.8 |  |  |  | 0.8
10 |  |  |  | 0.15 |  |  | 0.15 | 15:45 |  |  |  | 0.5 |  |  | 0.5
11 |  |  |  |  | 0.2 |  | 0.2 | 19:30 |  |  |  |  | 0 |  | 0
12 |  |  | 0.23 |  |  |  | 0.23 | 11:00 |  |  | 0.5 |  |  |  | 0.5
13 |  |  | 0.33 |  |  |  | 0.33 | 10:00 |  |  | 0.5 |  |  |  | 0.5
14 |  | 0.28 |  |  |  |  | 0.28 | 7:30 |  | 0.6 |  |  |  |  | 0.6
15 |  |  |  |  | 0.14 |  | 0.14 | 16:00 |  |  |  |  | 1.5 |  | 1.5
16 |  |  |  |  | 0.25 |  | 0.25 | 16:00 |  |  |  |  | 1.3 |  | 1.3
17 |  |  |  | 0.25 |  |  | 0.25 | 14:30 |  |  |  | 1.5 |  |  | 1.5
18 |  |  | 0.23 |  |  |  | 0.23 | 9:40 |  |  | 0.7 |  |  |  | 0.7
19 |  |  |  |  | 0.29 |  | 0.29 | 16:30 |  |  |  |  | 0.6 |  | 0.6
20 |  |  |  |  | 0.28 |  | 0.28 | 16:00 |  |  |  |  | 1 |  | 1
21 | [5 empty] | 0.26 | 0.26 | 20:20 | [5 empty] | 1 | 1
22 |  |  | 0.24 |  |  |  | 0.24 | 11:00 |  |  | 1 |  |  |  | 1
23 |  |  |  | 0.16 |  |  | 0.16 | 15:00 |  |  |  | 1 |  |  | 1
24 |  |  |  | 0.2 |  |  | 0.2 | 15:15 |  |  |  | 1 |  |  | 1
25 |  |  | 0.22 |  |  |  | 0.22 | 11:00 |  |  | 1 |  |  |  | 1
26 |  |  |  |  | 0.14 |  | 0.14 | 17:00 |  |  |  |  | 1.2 |  | 1.2
27 |  |  |  |  | 0.18 |  | 0.18 | 16:30 |  |  |  |  | 1.1 |  | 1.1
28 |  |  |  |  | 0.2 |  | 0.2 | 16:00 |  |  |  |  | 1.1 |  | 1.1
29 |  |  |  |  | 0.18 |  | 0.18 | 17:50 |  |  |  |  | 1 |  | 1
30 |  |  |  | 0.2 |  |  | 0.2 | 15:30 |  |  |  | 1 |  |  | 1
31 |  |  |  | 0.24 |  |  | 0.24 | 15:30 |  |  |  | 1.1 |  |  | 1.1
| *If the plant is offline input "PO" in the blank | [7 empty] | *If at ANY time the entry point residual chlorine falls below 0.2 mg/L, the system must call the SWTR Manager. | [7 empty] | Version 2009c.1
Continuous Sampling
Grab Sampling
Continuous Sampling
Grab Sampling