IMPORTANT INFORMATION ABOUT YOUR DRINKING WATER

## Meadow Mountain Water Supply

Did Not Meet Treatment Requirements

Our water system recently violated a drinking water standard. Although this was not an emergency, as our

Customers, you have a right to know what happened, what you should do, and what we did to correct this situation.

We routinely monitor your water for turbidity (cloudiness). This tells us whether we are effectively filtering the

water supply.  Water samples for (month)___MAY_____ showed that (percentage) _____29%___ percent of turbidity

measurements were over 1.0 turbidity units.  The standard is that no more than 5 percent of samples may exceed 1

turbidity units per month. Normal turbidity levels at our plant are (number)_____<1.0_________ units.

What does this mean?  What should I do?

You do not need to boil your water or take other actions. We do not know of any contamination, and

none of our testing has shown disease-causing organisms in the drinking water.

People with severely compromised immune systems, infants, and some elderly may be at increased risk.

These people should seek advice about drinking water from their health care providers. General guidelines

on ways to lessen the risk of infection by microbes are available from EPA’s Safe Drinking Water Hotline

at 1 (800) 426-4791.

Inadequately treated water may contain disease-causing organisms.  These organisms include bacteria,

viruses, and parasites which can cause symptoms such as nausea, cramps, diarrhea, and associated

headaches.  These symptoms, however, are not caused only by organisms in drinking water.  If you

experience any of these symptoms and they persist, you may want to seek medical advice.

Turbidity has no health effects. However, turbidity can interfere with disinfection and provide a medium

for microbial growth. Turbidity may indicate the presence of disease causing organisms. These organisms

include bacteria, viruses, and parasites which can cause symptoms such as nausea, cramps, diarrhea, and

associated headaches. These symptoms are not caused only by organisms in drinking water. If you

experience any of these symptoms and they persist, you may want to seek medical advice.

What happened? What was done?

A problem occurred with the treatment system at the water plant.

(Describe the reason for high turbidity and corrective action)

The high turbidity was due to seasonal runoff. This turbidity issue is due to the slight ‘tea colored’ water that we experience during seasonal runoff periods as the test for turbidity not only picks up particles in the water but it also recognizes color as turbidity.  This is a phenomenon that we have been experiencing for several years and we are continuously investigating alternative solutions for this color issue.  This year we tried a new Turbidity Meter to determine if newer technology would help to remove the color issue from our test results, but this new Turbidity Meter gave us the exact same test results as our existing Turbidity Meter.______________________________

We anticipate resolving the problem within (estimated time frame) the month of May_____________.  For more

information, please contact (name of contact) __Rachel Barkworth_______________ at (phone number)

_____303-823-2318___ or (mailing address) P.O. Box 354, Allenspark, Co, 80510.

Please share this information with all the other people who drink this water, especially those who may not have

received this notice directly (for example, people in apartments, nursing homes, schools, and businesses). You can

do this by posting this notice in a public place or distributing copies by hand or mail.

This notice is being sent to you by (system name) _Meadow Mountain Water Supply___.

Colorado Public Water System ID #: __CO-0207504___________ Date distributed: _June 2010.