## Summary
System Name: |  | MEADOW MOUNTAIN WS | [5 empty] | Treatment: |  | Slow Sand/DE/Other
PWSID: |  | CO0207504 |  | Monitoring Period (Month/ Year): | [5 empty] | 2013-09-01
State Assigned ID (Plant ID): |  |  | 001
Plant Address: |  | 137 Meadow Mountain Drive |  |  |  | City: | Allenspark |  |  |  |  | Zip: | 80510
Contact Name: |  | Rachel Barkworth |  |  |  | Phone#: |  | 303-823-2318
Combined Filter Effluent Turbidity (CFE) Summary: | [8 empty] | Violation? | Plant off entire month:
↓
| Number of Samples Required*: | [5 empty] | 30
| Number of Samples Taken: | [5 empty] | 30 |  | No
| Number of Samples Exceeding 5 NTU: | [5 empty] | 0 |  | No
| Highest Single Turbidity Reading: | [5 empty] | 5.32 |  | No
| Number of Samples Exceeding 1 NTU (95% limit): | [5 empty] | 6 |  | Yes
| % of Samples Exceeding 1 NTU: | [5 empty] | 20% |  | Yes
Entry Point Residual Disinfectant (EPRD) Summary: | [5 empty] | State Assigned ID: |  |  | 001 |  |  | Violation? | For Use by State:
For Chlorine or Chloramine
↓
| Number of Samples Required: | [9 empty] | 30
| Number of Samples Taken: | [9 empty] | 31 | No
| Number of Samples under 0.2 mg/L (Federal level): | [9 empty] | 1 | Yes
| If applicable, number of Samples under |  |  | _____ | mg/L (State Defined level):
= Required for data processing
number required per day
X
number of days in month
number of plant offlines (PO)
minus
*Samples Required=
Free
Total

## Data Sheet
System Name: |  |  | MEADOW MOUNTAIN WS |  |  |  |  | PWSID: | CO0207504 |  | State Assigned ID: |  |  | 001 | Monitoring Period: |  | 2013-09-01
Required Number of Turbidity Readings Per Day: | [6 empty] | 1 |  | Required Number of Chlorine Readings Per Day: | [6 empty] | 1
| Combined Filter Effluent Turbidity (NTU) | [7 empty] | Entry Point Residual Disinfection (mg/L) | [6 empty] | Comments*
Day | 12-4a Time: ___ | 4a-8a Time: ___ | 8a-12 Time: _____ | 12-4p Time: ____ | 4p-8p Time: ____ | 8p-12 Time: ____ | Highest Turbidity Reading | Highest Reading Time | 12-4a Time: ______ | 4a-8a Time: ______ | 8a-12 Time: ______ | 12-4p Time: ______ | 4p-8p Time: ______ | 8p-12 Time: ______ | Lowest Residual Reading
1 |  |  | 0.46 |  |  |  | 0.46 | 10:40 |  |  | 0.8 |  |  |  | 0.8
2 |  |  | 0.37 |  |  |  | 0.37 | 10:45 |  |  | 0.8 |  |  |  | 0.8
3 |  |  | 0.31 |  |  |  | 0.31 | 11:00 |  |  | 0.8 |  |  |  | 0.8
4 |  |  |  | 0.59 |  |  | 0.59 | 15:30 |  |  |  | 0.8 |  |  | 0.8
5 |  |  |  | 0.33 |  |  | 0.33 | 15:00 |  |  |  | 1.1 |  |  | 1.1
6 |  |  | 0.35 |  |  |  | 0.35 | 11:30 |  |  | 1.3 |  |  |  | 1.3
7 |  |  |  | 0.38 |  |  | 0.38 | 14:30 |  |  |  | 1.2 |  |  | 1.2
8 |  |  |  | 0.32 |  |  | 0.32 | 12:30 |  |  |  | 1 |  |  | 1
9 |  |  | 0.49 |  |  |  | 0.49 | 9:30 |  |  | 1.3 |  |  |  | 1.3
10 |  |  |  | 0.44 |  |  | 0.44 | 15:00 |  |  |  | 1.3 |  |  | 1.3
11 |  |  |  | 0.42 |  |  | 0.42 | 14:00 |  |  |  | 1.3 |  |  | 1.3
12 |  |  |  |  | 0.62 |  | 0.62 | 18:30 |  |  |  |  | 0.9 |  | 0.9
13 |  |  |  | 0.94 |  |  | 0.94 | 15:00 |  |  |  | 0.3 |  |  | 0.3
14 |  |  |  |  | 5.32 |  | 5.32 | 16:15 |  |  |  |  | 0.5 |  | 0.5
15 |  |  |  | 2.44 |  |  | 2.44 | 12:30 |  |  |  | 0 | 1.2 |  | 0 | Second Reading was at 13:30, Changed Chlorine Pump
16 |  |  |  | 2.05 |  |  | 2.05 | 15:30 |  |  | 1.4 |  |  |  | 1.4
17 |  |  |  | 2.58 |  |  | 2.58 | 15:30 |  |  |  | 1.2 |  |  | 1.2
18 |  |  | 1.98 |  |  |  | 1.98 | 11:00 |  |  | 1.4 |  |  |  | 1.4
19 |  |  |  | 1.8 |  |  | 1.8 | 12:15 |  |  |  | 1.7 |  |  | 1.7 | Installed Sunspring System
20 |  |  |  | 1.01 |  |  | 1.01 | 13:00 |  |  |  | 2 |  |  | 2
21 |  |  |  |  | 1.1 |  | 1.1 | 16:00 |  |  |  |  | 3.2 |  | 3.2
22 |  |  | 0.76 |  |  |  | 0.76 | 8:00 |  |  | 3.5 |  |  |  | 3.5
23 |  |  |  |  | 0.62 |  | 0.62 | 16:00 |  |  |  |  | 1.5 |  | 1.5
24 |  |  | 0.32 |  |  |  | 0.32 | 9:10 |  |  | 0.5 |  |  |  | 0.5
25 |  |  |  | 0.25 |  |  | 0.25 | 15:20 |  |  |  | 0.7 |  |  | 0.7 | Installed second Sunspring System
26 |  |  |  |  | 0.25 |  | 0.25 | 16:30 |  |  |  | 2.5 |  |  | 2.5
27 |  |  |  | 0.22 |  |  | 0.22 | 14:45 |  |  |  | 2 |  |  | 2
28 |  |  |  | 0.24 |  |  | 0.24 | 15:30 |  |  |  | 2 |  |  | 2
29 |  |  | 0.62 |  |  |  | 0.62 | 20:55 |  |  | 2.5 |  |  |  | 2.5
30 |  |  |  |  | 0.54 |  | 0.54 | 18:20 |  |  |  |  | 1.8 |  | 1.8
31
| *If the plant is offline input "PO" in the blank | [7 empty] | *If at ANY time the entry point residual chlorine falls below 0.2 mg/L, the system must call the SWTR Manager. | [7 empty] | Version 2009c.1
Continuous Sampling
Grab Sampling
Continuous Sampling
Grab Sampling