## Summary
Monthly Operating Report (MOR) Summary Form Submit Online at www.wqcdcompliance.com/login
Yellow Background = PWS Input Value |  |  | Blue Background = Calculated Value |  |  | Red Background = Violation
Public Water System Information Section
PWS ID: | CO0207504 | PWS Name: | Meadow Mtn Water Supply | MOR Type: |  | Membrane
Facility ID: | 001 | Facility Name: | Meadow Mtn SWTP01 | Month: | Jul (7) |  | Year: | 2018
Contact Person: | Rachel Barkworth | Email: | rcbarkworth@yahoo.com | Phone: | 303-823-2318 |  | Save as In-Progress (xlsm)
Comments:
Turbidity Combined Filter Effluent (CFE) Summary Section *If at ANY time the turbidity rises above 0.5 NTU the PWS must contact the department within 24 hours.
Facility ID: | 001 |  | Required Number of Samples Per Day: |  |  | 1
Number of Samples Required: |  | 31 | Number of Samples Taken: |  | 31 | Number of Plant Offs: |  | 0
Number of Days Sampling Required: |  | 31 | Number of Days Sampling Met: |  | 31 | M&R Complied: |  | Yes
Number of Samples Exceeding 0.5 NTU: |  | 0 | Highest Sample: |  | 0.028 | Max TT Complied: |  | Yes
Number of Samples Exceeding 0.1 NTU: |  | 0 | % Samples Exceeding: |  | 0 | 95% TT Complied: |  | Yes
Microbial Treatment - Minimum Disinfection Summary Section *If at ANY time the residual falls below 1.2 mg/L the PWS must contact the department within 48 hours.
Facility ID: | 001 |  | Required Number of Samples Per Day: |  |  | 1
Number of Samples Required: |  | 31 | Number of Samples Taken: |  | 31 | Number of Plant Offs: |  | 0
Number of Days Sampling Required: |  | 31 | Number of Days Sampling Met: |  | 31 | M&R Complied: |  | Yes
Number of Samples Below 1.2 mg/L: |  | 0 | Lowest Sample: |  | 1.3 | Min TT Complied: |  | Yes
Longest Duration Below Minimum: |  | N/A (No Values Below Minimum)
Revision: 5/17/2015
MOR
Calculate
Calculate

## DataSheet
Monthly Operating Report (MOR) - Data Sheet
PWS: CO0207504 - Meadow Mtn Water Supply | [7 empty] | Facility: 001 - Meadow Mtn SWTP01 | [5 empty] | Time Period: Jul (7) - 2018
Accepted Values: Numeric >= 0, NS (No Sample), and PO (Plant Off). Blanks automatically converted to NS. C (Continuous) is allowed for Disinfection time periods only. If used, the Lowest Residual Sample Column must be completed.
Day | Combined Filter Effluent Turbidity (NTU) *Highest Hourly & Daily Value Must be Entered* | [6 empty] | Microbial Disinfection (mg/L) *Lowest Daily Value Must be Entered* | [6 empty] | Minimum mg/L: | 1.2
| 12a-4a | 4a-8a | 8a-12p | 12p-4p | 4p-8p | 8p-12a | Highest Turbidity Sample | 12a-4a | 4a-8a | 8a-12p | 12p-4p | 4p-8p | 8p-12a | Lowest Residual Sample | Longest Duration Below Minimum
[15 empty] | Hours | Minutes
1 | NS | 0.027 | NS | NS | NS | NS | 0.027 | NS | 1.3 | NS | NS | NS | NS | 1.3
2 | NS | 0.027 | NS | NS | NS | NS | 0.027 | NS | 1.3 | NS | NS | NS | NS | 1.3
3 | NS | NS | 0.027 | NS | NS | NS | 0.027 | NS | NS | 1.5 | NS | NS | NS | 1.3
4 | NS | NS | NS | NS | 0.027 | NS | 0.027 | NS | NS | NS | NS | 1.6 | NS | 1.3
5 | NS | NS | NS | NS | 0.027 | NS | 0.027 | NS | NS | NS | NS | 1.5 | NS | 1.4
6 | NS | NS | 0.027 | NS | NS | NS | 0.027 | NS | NS | 1.5 | NS | NS | NS | 1.4
7 | NS | NS | NS | 0.027 | NS | NS | 0.027 | NS | NS | NS | 1.6 | NS | NS | 1.5
8 | NS | NS | NS | 0.027 | NS | NS | 0.027 | NS | NS | NS | 1.5 | NS | NS | 1.4
9 | NS | NS | 0.028 | NS | NS | NS | 0.028 | NS | NS | 1.5 | NS | NS | NS | 1.4
10 | NS | NS | 0.028 | NS | NS | NS | 0.028 | NS | NS | 1.6 | NS | NS | NS | 1.4
11 | NS | NS | 0.028 | NS | NS | NS | 0.028 | NS | NS | 1.8 | NS | NS | NS | 1.4
12 | NS | NS | NS | NS | NS | 0.027 | 0.027 | NS | NS | NS | NS | NS | 1.6 | 1.5
13 | NS | NS | NS | NS | 0.027 | NS | 0.027 | NS | NS | NS | NS | 1.7 | NS | 1.5
14 | NS | NS | 0.026 | NS | NS | NS | 0.026 | NS | NS | 1.7 | NS | NS | NS | 1.5
15 | NS | NS | NS | NS | 0.027 | NS | 0.027 | NS | NS | NS | NS | 1.6 | NS | 1.4
16 | NS | NS | NS | 0.027 | NS | NS | 0.027 | NS | NS | NS | 1.5 | NS | NS | 1.4
17 | NS | NS | 0.026 | NS | NS | NS | 0.026 | NS | NS | 1.5 | NS | NS | NS | 1.4
18 | NS | NS | 0.027 | NS | NS | NS | 0.027 | NS | NS | 1.8 | NS | NS | NS | 1.5
19 | NS | NS | NS | NS | 0.026 | NS | 0.026 | NS | NS | NS | NS | 1.7 | NS | 1.5
20 | NS | NS | NS | NS | 0.027 | NS | 0.027 | NS | NS | NS | NS | 1.7 | NS | 1.4
21 | NS | NS | 0.026 | NS | NS | NS | 0.026 | NS | NS | 1.6 | NS | NS | NS | 1.5
22 | NS | NS | NS | NS | 0.026 | NS | 0.026 | NS | NS | NS | NS | 1.6 | NS | 1.4
23 | NS | NS | NS | NS | 0.027 | NS | 0.027 | NS | NS | NS | NS | 1.6 | NS | 1.4
24 | NS | NS | 0.027 | NS | NS | NS | 0.027 | NS | NS | 1.4 | NS | NS | NS | 1.4
25 | NS | NS | 0.026 | NS | NS | NS | 0.026 | NS | NS | 1.6 | NS | NS | NS | 1.4
26 | NS | NS | NS | NS | 0.027 | NS | 0.027 | NS | NS | NS | NS | 1.6 | NS | 1.4
27 | NS | 0.026 | NS | NS | NS | NS | 0.026 | NS | 1.6 | NS | NS | NS | NS | 1.4
28 | NS | NS | NS | NS | 0.026 | NS | 0.026 | NS | NS | NS | NS | 1.5 | NS | 1.5
29 | NS | NS | NS | 0.026 | NS | NS | 0.026 | NS | NS | NS | 1.6 | NS | NS | 1.5
30 | NS | NS | 0.026 | NS | NS | NS | 0.026 | NS | NS | 1.5 | NS | NS | NS | 1.5
31 | NS | NS | 0.026 | NS | NS | NS | 0.026 | NS | NS | 1.8 | NS | NS | NS | 1.8
Note on Q5: Duration required when value is below minimum.

## Lookup (hidden)
Month | Answer | Facilty Type | 95% Turbidity | Max Turbidity | Daily Frequency | Hours | Minutes | Save Options
Jan (1) | Yes | Bag/Cartridge | 1 | 5 | 0 | 0 | 0 | Save as In-Progress (xlsm)
Feb (2) | No | Conventional/Direct | 0.3 | 1 | 1 | 1 | 1 | Save as Final State (xlsx)
Mar (3) | N/A | Membrane | 0.1 | 0.5 | 2 | 2 | 2
Apr (4) |  | Slow Sand/Diatomaceous Earth | 1 | 5 | 3 | 3 | 3
May (5) |  | Disinfection Only | N/A | N/A | 4 | 4 | 4
Jun (6) |  |  |  |  | 5 | 5 | 5
Jul (7) |  |  |  |  | 6 | 6 | 6
Aug (8) | [5 empty] | 7 | 7
Sep (9) | [5 empty] | 8 | 8
Oct (10) | [5 empty] | 9 | 9
Nov (11) | [5 empty] | 10 | 10
Dec (12) | [5 empty] | 11 | 11
[6 empty] | 12 | 12
[6 empty] | 13 | 13
[6 empty] | 14 | 14
[6 empty] | 15 | 15
[6 empty] | 16 | 16
[6 empty] | 17 | 17
[6 empty] | 18 | 18
[6 empty] | 19 | 19
[6 empty] | 20 | 20
[6 empty] | 21 | 21
[6 empty] | 22 | 22
[6 empty] | 23 | 23
[6 empty] | 24 | 24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59