MEADOW MTN WATER SUPPLY 2015 Drinking Water Quality Report 
For Calendar Year 2014 
Public Water System ID: CO0207504
Esta es información importante.  Si no la pueden leer, necesitan que alguien se la traduzca.

We are pleased to present to you this year’s water quality report.  Our constant goal is to provide you with a safe and dependable supply of drinking water.  Please contact RACHEL BARKWORTH at 303-823-2318 with any questions about the Drinking Consumer Confidence Rule (CCR) or for public participation opportunities that may affect the water quality.

General Information
All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water Hotline (1-800-426-4791) or by visiting http://water.epa.gov/drink/contaminants.

Some people may be more vulnerable to contaminants in drinking water than the general population.  Immunocompromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV-AIDS or other immune system disorders, some elderly, and infants can be particularly at risk of infections.  These people should seek advice about drinking water from their health care providers.  For more information about contaminants and potential health effects, or to receive a copy of the U.S. Environmental Protection Agency (EPA) and the U.S. Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and microbiological contaminants call the EPA Safe Drinking Water Hotline at (1-800-426-4791).

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity. Contaminants that may be present in source water include:

•Microbial contaminants: viruses and bacteria that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
•Inorganic contaminants: salts and metals, which can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
•Pesticides and herbicides: may come from a variety of sources, such as agriculture, urban stormwater runoff, and residential uses.
•Radioactive contaminants: can be naturally occurring or be the result of oil and gas production and mining activities.
•Organic chemical contaminants: including synthetic and volatile organic chemicals, which are byproducts of industrial processes and petroleum production, and also may come from gas stations, urban storm water runoff, and septic systems.

In order to ensure that tap water is safe to drink, the Colorado Department of Public Health and Environment prescribes regulations limiting the amount of certain contaminants in water provided by public water systems.  The Food and Drug Administration regulations establish limits for contaminants in bottled water that must provide the same protection for public health. 

Lead in Drinking Water
If present, elevated levels of lead can cause serious health problems (especially for pregnant women and young children). It is possible that lead levels at your home may be higher than other homes in the community as a result of materials used in your home’s plumbing. If you are concerned about lead in your water, you may wish to have your water tested. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. Additional information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at http://www.epa.gov/safewater/lead. 

Source Water Assessment and Protection (SWAP)
The Colorado Department of Public Health and Environment has provided us with a Source Water Assessment Report for our water supply. For general information or to obtain a copy of the report please visit http://wqcdcompliance.com/ccr.  The report is located under “Source Water Assessment Reports”, and then “Assessment Report by County”.  Select BOULDER County and find 207504; MEADOW MTN WATER SUPPLY or by contacting RACHEL BARKWORTH at 303-823-2318.  The Source Water Assessment Report provides a screening-level evaluation of potential contamination that could occur. It does not mean that the contamination has or will occur. We can use this information to evaluate the need to improve our current water treatment capabilities and prepare for future contamination threats. This can help us ensure that quality finished water is delivered to your homes. In addition, the source water assessment results provide a starting point for developing a source water protection plan.  Potential sources of contamination in our source water area are listed on the next page.

Please contact us to learn more about what you can do to help protect your drinking water sources, any questions about the Drinking Water Consumer Confidence Report, to learn more about our system, or to attend scheduled public meetings. We want you, our valued customers, to be informed about the services we provide and the quality water we deliver to you every day.

Our Water Sources

| Source | Source Type | Water Type | Potential Source(s) of Contamination |
| --- | --- | --- | --- |
| WILLOW CREEK | Intake | Surface Water | Animals in the stream, tree debris |
| FOX CREEK | Intake | Surface Water | Animals in the stream, tree debris |

Terms and Abbreviations

- Maximum Contaminant Level (MCL) − The highest level of a contaminant allowed in drinking water.

- Treatment Technique (TT) − A required process intended to reduce the level of a contaminant in drinking water.

- Action Level (AL) − The concentration of a contaminant which, if exceeded, triggers treatment and other regulatory requirements.

- Maximum Residual Disinfectant Level (MRDL) − The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

- Maximum Contaminant Level Goal (MCLG) − The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

- Maximum Residual Disinfectant Level Goal (MRDLG) − The level of a drinking water disinfectant, below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

- Violation (No Abbreviation) − Failure to meet a Colorado Primary Drinking Water Regulation.

- Formal Enforcement Action (No Abbreviation) − Escalated action taken by the State (due to the risk to public health, or number or severity of violations) to bring a non-compliant water system back into compliance.

- Variance and Exemptions (V/E) − Department permission not to meet a MCL or treatment technique under certain conditions.

- Gross Alpha (No Abbreviation) − Gross alpha particle activity compliance value. It includes radium-226, but excludes radon 222, and uranium.

- Picocuries per liter (pCi/L) − Measure of the radioactivity in water.

- Nephelometric Turbidity Unit (NTU) − Measure of the clarity or cloudiness of water. Turbidity in excess of 5 NTU is just noticeable to the typical person.

- Compliance Value (No Abbreviation) – Single or calculated value used to determine if regulatory contaminant level (e.g.  MCL) is met. Examples of calculated values are the 90th Percentile, Running Annual Average (RAA) and Locational Running Annual Average (LRAA).

- Average (x-bar) − Typical value.

- Range (R) − Lowest value to the highest value.

- Sample Size (n) − Number or count of values (i.e. number of water samples collected).

- Parts per million = Milligrams per liter (ppm = mg/L) − One part per million corresponds to one minute in two years or a single penny in $10,000.

- Parts per billion = Micrograms per liter (ppb = ug/L) − One part per billion corresponds to one minute in 2,000 years, or a single penny in $10,000,000.

- Not Applicable (N/A) – Does not apply or not available.

Detected Contaminants

MEADOW MTN WATER SUPPLY routinely monitors for contaminants in your drinking water according to Federal and State laws. The following table(s) show all detections found in the period of January 1 to December 31, 2014 unless otherwise noted. The State of Colorado requires us to monitor for certain contaminants less than once per year because the concentrations of these contaminants are not expected to vary significantly from year to year, or the system is not considered vulnerable to this type of contamination. Therefore, some of our data, though representative, may be more than one year old. Violations and Formal Enforcement Actions, if any, are reported in the next section of this report.

Note: Only detected contaminants sampled within the last 5 years appear in this report. If no tables appear in this section then no contaminants were detected in the last round of monitoring.

| Lead and Copper Sampled in the Distribution System |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Contaminant Name | Time Period | 90th Percentile | Sample Size | Unit of Measure | 90th Percentile AL | Sample Sites Above AL | 90th Percentile AL Exceedance | Typical Sources |
| Copper | 06/23/2013 to 06/23/2013 | 0.3 | 5 | Ppm | 1.3 |  | No | Corrosion of household plumbing systems; Erosion of natural deposits |
| Lead | 06/23/2013 to 06/23/2013 | 23 | 5 | Ppb | 15 | 1 | Yes | Corrosion of household plumbing systems; Erosion of natural deposits |

| Disinfection Byproducts Sampled in the Distribution System |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Name | Year | Average | Range Low – High | Sample Size | Unit of Measure | MCL | MCLG | Highest Compliance Value | MCL Violation | Typical Sources |
| Total Haloacetic Acids (HAA5) | 2013 | 5.1 | 5.1 to 5.1 | 1 | Ppb | 60 | N/A | ** See Notes | No | Byproduct of drinking water disinfection |
| Total Trihalomethanes (TTHM) | 2013 | 34 | 34 to 34 | 1 | Ppb | 80 | N/A | ** See Notes | No | Byproduct of drinking water disinfection |

| Summary of Turbidity Sampled at the Entry Point to the Distribution System |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Contaminant Name | Sample Date | Level Found | TT Requirement | TT Violation | Typical Sources |
| Turbidity | Date/Month: April | Highest single measurement: 1.85 NTU | Maximum 5 NTU for any single measurement | Yes | Soil Runoff |
| Turbidity | Month: April | Lowest monthly percentage of samples meeting TT requirement for our technology: 13 % | In any month, at least 95% of samples must be less than 1 NTU | Yes | Soil Runoff |

| Radionuclides Sampled at the Entry Point to the Distribution System |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Contaminant Name | Year | Average | Range Low – High | Sample Size | Unit of Measure | MCL | MCLG | MCL Violation | Typical Sources |
| Gross Alpha | 2011 | 0.03 | 0.03 to 0.03 | 1 | pCi/L | 15 | 0 | No | Erosion of natural deposits |
| Combined Radium | 2011 | 0.34 | 0.34 to 0.34 | 1 | pCi/L | 5 | 0 | No | Erosion of natural deposits |
| Combined Uranium | 2011 | 0.1 | 0.1 to 0.1 | 1 | ppb | 30 | 0 | No | Erosion of natural deposits |

Violations, Significant Deficiencies, and Formal Enforcement Actions

| Violations |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Name | Category | Time Period | Health Effects | Compliance Value | TT Level or MCL |
| VOLATILE ORGANICS | MONITORING, ROUTINE MAJOR - MONITORING & REPORTING | 01/01/2014 - 12/31/2014 | N/A | N/A | N/A |
| TURBIDITY | MONTHLY COMB FLTR EFFLUENT (IESWTR/LT1) - TREATMENT TECHNIQUE | 04/01/2014 - 04/30/2014 | Turbidity has no health effects. However, turbidity can interfere with disinfection and provide a medium for microbial growth. Turbidity may indicate the presence of disease-causing organisms. These organisms include bacteria, viruses, and parasites that can cause symptoms such as nausea, cramps, diarrhea and associated headaches. | 0 N/A | N/A |
| TOTAL TRIHALOMETHANES (TTHM) | MONITORING, ROUTINE (DBP), MAJOR - MONITORING & REPORTING | 01/01/2014 - 12/31/2014 | N/A | N/A | N/A |
| TOTAL HALOACETIC ACIDS (HAA5) | MONITORING, ROUTINE (DBP), MINOR - MONITORING & REPORTING | 01/01/2014 - 12/31/2014 | N/A | N/A | N/A |
| NITRATE | MONITORING, ROUTINE MAJOR - MONITORING & REPORTING | 01/01/2014 - 12/31/2014 | N/A | N/A | N/A |
| Additional Violation Information |  |  |  |  |  |
| Note: If any violation relates to failing to install adequate filtration or disinfection equipment or processes, or have had a failure of such equipment or processes then the water may be inadequately treated. Inadequately treated water may contain disease-causing organisms. These organisms include bacteria, viruses, and parasites, which can cause symptoms such as nausea, cramps, diarrhea, and associated headaches. Explanation of the violation(s) and the steps taken to resolve them: |  |  |  |  |  |
| Explanatory Notes for Violations: The four violations that are categorized as “MONITORING, ROUTINE”, whether MAJOR or MINOR are due to a miscommunication between the lab that MMWSC was using for the testing and the Colorado Department of Public Health and Environment related to their paperwork, documentation and certification. The lab has corrected the deficiency, but we were assigned a violation for not knowing that the lab supposedly no longer had their certification to allow them to perform the tests accurately. We did perform the tests and we did receive results from those test. Those results were submitted to the CDPHE. We have changed the lab that we are using so that we do not have to deal with a lab that cannot keep its certification requirements current. The results that are shown in this report are the test results from 2013; we will not be able to remove the violation until we perform these same tests in 2015, using the new lab. The Turbidity Violation was encountered in April during our early run-off period, and these results are prior to installing the new ultra-filtration system. Enforcement Order Notification – if you have not already received our notification regarding the removal of the Enforcement Order that was placed on MMWSC in August 2011, please take note that this enforcement order has now been removed as we have taken all the necessary steps required by CDPHE. If you have any questions regarding this information, please do not hesitate to contact RACHEL BARKWORTH at (303) 823-2318 or via email at RCBarkworth@Yahoo.com. |  |  |  |  |  |